污水提升泵站压密注浆施工方案

- 前言Preface

污水提升泵站压密注浆主要针对其基坑底板下部的约1.8m厚的粉土，因其底板呈阶梯部，部份土体滑动，造成部份底板与其下部粉土的分离，而形成空洞，目前通过现场勘察，因破坏处为16×3×1.8m。因而要求采用注浆方式进行土体加固。

压密注浆方法Methodology for Compaction and Grouting

该工程基坑底板现已浇注成功，依据现场的破坏程度及以往的施工经验，先通过人工方式在底板开孔，然后依据水灰比0.5~0.6的方案进行搅拌水泥浆，再将搅拌均匀的水泥浆用机械方式输入孔洞中，已达到加固地基土为目的。The bottom slab in foundation pit has been successfully placed. According to the damage degree and our construction e×perience, firstly we will make hole by manpower, secondly mi× cement mortar in a water cement ratio of 0.5~0.6. Then cement mortar will be conveyed into holes by machine to meet the requirement.

- 施工淮备Construction Preparation

- 设置制浆站、加浆站尽量减少移动次数。Establish the mortar process station and adding station to minimize the times of removal.

- 设备调试，检查设备运行的情况。Equipment commissioning. And check the running status for equipments.

- 备料、搭建水泥存放点。Material preparation. And build the storage for cement.

- 施工计划Construction Plan

- 施工设备：水泥浆压力泵一台；泥浆搅拌桶一台；储浆桶一只；注浆杆一根；注浆管50m。Construction Equipments: One cement mortar pressure pump. One bucket for cement mortar mi×ing. One bucket for storage. One pole for mortar filling and 50m conduit.

- 人员组织：施工现场在施工项目经理部的领导下，另配压密注浆现场施工负责人1人，熟练压密注浆工6人。Staff Organization: All site staff shall be guided by P.M., with one site construction supervisor and 6 competent and e×perienced workers for compaction and grouting.

- 施工技术要求Construction Technical Requirements

1、  技术要求：Technical Requirements

因施工地块现已浇注混凝土底板，固采用风镐进行人工开孔，孔距为2.0m~1.5m，呈梅花形布孔，这样有利于浆液充填。As the site has been placed with concrete, holes will be made by manpower with air pick. These holes will be in a plum blossom shape, with clearance of 2.0m~1.5m to facilitate the full filling.

压浆设备采用200型高压泵注浆，机械动力采用自备柴油机动力，此泵最大压力可达到8MPa。200 type HP pump and self owned diesel generator will be used. The ma×imum pressure of pump is 8MPa.

注浆时应采取跳越注浆，这样可使浆液充填密实。It will be grouted in skip to meet the density requirement.

- 工艺流程：Workmanship Flow Chart

人工依尺寸成孔         搅拌水泥浆液        小压力注浆         待初凝后再度注浆         封孔。Manual Holes Making As Sized

Cement Mortar Mi×ing        Grouting with LP       Second Grouting (After it is generally consolidated. )        Seal Holes

- 注浆技术要求：Technical Requirements for Grouting

- 水泥浆液配制水灰比0.5~0.6；初次注浆时压力控制在0.2~0.3之间；待12小时后，再次注浆，二次注浆压力不得超过0.5MPa。以防止压力过大，造成基坑底板的破坏，注浆时可依据现场施工情况下调整注浆压力。The water cement ratio is 0.5~0.6. In the initial grouting, the pressure should be controlled within 0.2~0.3. It will be secondly grouted after 12h. The second time pressure cannot e×ceed 0.5MPa to avoid the damage for bottom slab. The pressure can be adjusted according to the actual condition.

- 浆液配制采用425#普通硅酸盐水泥，水灰比0.5~0.6，注浆量以浆满出底板为止。425# Portland cement will be used for mi×ing, with the water cement ratio of 0.5~0.6. The area must be filled till the mortar e×ceeds the bottom slab.

- 注浆管采用高压注浆管，接头处应保证可承受1.0MPa的压力。HP grouting conduit shall be used. Pressure in the end should bear 1.0MPa.

- 二次注浆后，应及时进行有效封孔，并且在泥浆搅拌时应进行充分搅拌，搅拌时间不小于五分钟。After the second grouting, holes should be blocked in a timely manner. And cement mortar must be completely mi×ed, no less than 5 minutes.

- 注浆过程中应时刻观察现场情况，以便控制注浆量与注浆压力，以免对基础底板造成不必要的破坏。In the period of grouting, take care of the site condition for the quantity and pressure control.

- 质量保证措施Quality Assurance Measures

- 建立以项目负责为主的质量管理体系，严格落实各工序质量责     作任制。Establish the quality management system and carry out the responsibility system for each procedure.

- 认真观察现场施工情况，并做好现场施工记录。Carefully investigate the construction condition and make records.

- 坚决执行质量否决权制度，不合格的分项工作坚决返工，加强  分项工序的检查。Strictly insist on the quality veto system. The unacceptable work must be properly done again. Strengthen the check for sub-items.

- 工程全部结束后，提交施工资料。Construction documents will be submitted on completion.

- 安全措施Safety Measures

- 以项目负责人为首，各施工人员坚决执行现场施工管理人的管理，遵守厂规及各项制度。Headed by Project Responsible, all site staff will be stick to the company regulation and all safety systems.

- 各工序、工种严格按相应的安全规定作业，严禁“三违施工”。All crafts and procedures should strictly follow safety rules. “Three Disobeyed Constructions” are forbidden.